## WSFU
Department of Environmental Services-Development Engineering
WATER METER SIZING CHART
PROJECT NAME:
ADDRESS:
PERMIT NUMBER: |  | PREPARED BY:
FIXTURE TYPE |  | WATER UNIT (WU) FIXTURES |  | WATER SIZING FIXTURE UNITS (WSFU)
|  | Pre-development | Post-development | WU to WSFU Conversion Factor (from Building Code Table 6-5) | Post-development
Water Closet, 1.6 GPF - Gravity Tank |  |  |  | 2.5 | 0
Water Closet, 1.6 GPF - Flushometer Tank |  |  |  | 2.5 | 0
Water Closet, 1.6 GPF - Flushometer Valve |  |  |  | 5 | 0
Water Closet, greater than 1.6 GPF - Gravity Tank |  |  |  | 5.5 | 0
Water Closet, greater than 1.6 GPF - Flushometer Valve |  |  |  | 8 | 0
Urinal, 1.0 GPF |  |  |  | 4 | 0
Urinal, greater than 1.0 GPF |  |  |  | 5 | 0
Urinal, Flush tank |  |  |  | 2 | 0
Lavatory |  |  |  | 1 | 0
Bar sink |  |  |  | 2 | 0
Mop sink |  |  |  | 3 | 0
3 Compartment sink |  |  |  | 4 | 0
Laundry sink, Hand sink, Kitchen sink, & Prep sink |  |  |  | 1.5 | 0
Drinking fountain |  |  |  | 0.5 | 0
Dishwasher |  |  |  | 1.5 | 0
Clothes washer |  |  |  | 4 | 0
Bathtub (¾" fill valve) |  |  |  | 10 | 0
Shower |  |  |  | 2 | 0
Hose bib |  |  |  | 2.5 | 0
(2.5 for 1st and 1.0 for any additional) |  |  |  | 1 | 0
Other (List): |  |  |  |  | 0
Bathtub/Shower |  |  |  | 4 | 0
0
0
0
| TOTAL WUs & WSFUs: | 0 | 0 |  | 0
|  |  |  | WSFUs (GPM): | 0
CONTINUOUS FLOW (GPM):
|  |  |  | TOTAL FLOW (GPM): | 0
Required Minimum Service Line Size:
Required Minimum Water Meter Size:
Note on C11: Existing fixtures
Note on D11: Existing fixtures which will remain plus proposed new fixtures
Note on F39: A value must be entered in this cell.

## Curve Fit Data
Flushometer |  |  |  |  | Gravity
WSFU | GPM from Charts | Change from prev GPM | GPM from Formula | ∆ GPM | WSFU | GPM from Charts | Change from prev GPM | GPM from Formula | ∆ GPM
0 |  |  |  |  | 0 |  |  |  |  | CHART A-3
5 |  |  |  |  | 5
10 | 27 |  | 29.066 | 2.066 | 10 | 8 |  | 9.2719 | 1.2719
15 | 32 | 5 | 32.1508 | 0.15079 | 15 | 12 | 4 | 12.1401 | 0.14012
20 | 35 | 3 | 35.08 | 0.080048 | 20 | 15 | 3 | 14.8521 | -0.14788
25 | 38 | 3 | 37.8626 | -0.13739 | 25 | 18 | 3 | 17.4173 | -0.58269
30 | 41 | 3 | 40.507 | -0.49304 | 30 | 20 | 2 | 19.8447 | -0.15532
35 | 44 | 3 | 43.0213 | -0.97874 | 35 | 22 | 2 | 22.1429 | 0.14287
40 | 46 | 2 | 45.4133 | -0.58669 | 40 | 25 | 3 | 24.3202 | -0.67984
45 | 48 | 2 | 47.6906 | -0.30943 | 45 | 27 | 2 | 26.3845 | -0.61555
50 | 51 | 3 | 49.8602 | -1.1398 | 50 | 28 | 1 | 28.3433 | 0.34333
55 | 53 | 2 | 51.929 | -1.071 | 55 | 30 | 2 | 30.204 | 0.20402
60 | 55 | 2 | 53.9036 | -1.0964 | 60 | 32 | 2 | 31.9734 | -0.026552
65 | 56 | 1 | 55.7901 | -0.20992 | 65 | 34 | 2 | 33.6582 | -0.34181
70 | 58 | 2 | 57.5945 | -0.40554 | 70 | 36 | 2 | 35.2645 | -0.73545
75 | 59 | 1 | 59.3224 | 0.32238 | 75 | 37 | 1 | 36.7985 | -0.20151
80 | 60 | 1 | 60.9792 | 0.97922 | 80 | 38 | 1 | 38.2657 | 0.26572
85 | 62 | 2 | 62.5701 | 0.57008 | 85 | 40 | 2 | 39.6716 | -0.32837
90 | 64 | 2 | 64.0998 | 0.099836 | 90 | 41 | 1 | 41.0214 | 0.021369
95 | 65 | 1 | 65.5731 | 0.57308 | 95 | 42 | 1 | 42.3198 | 0.31979
100 | 67 | 2 | 66.9942 | -0.0058126 | 100 | 44 | 2 | 43.5715 | -0.42849
105 | 68 | 1 | 68.3673 | 0.36728 | 105 | 45 | 1 | 44.7809 | -0.21912
110 | 69 | 1 | 69.6963 | 0.69626 | 110 | 46 | 1 | 45.952 | -0.047986
115 | 70 | 1 | 70.9848 | 0.98482 | 115 | 47 | 1 | 47.0888 | 0.088782
120 | 72 | 2 | 72.2364 | 0.23641 | 120 | 48 | 1 | 48.1948 | 0.19483
125 | 73 | 1 | 73.4543 | 0.45432 | 125 | 49 | 1 | 49.2736 | 0.2736
130 | 74 | 1 | 74.6416 | 0.64159 | 130 | 50 | 1 | 50.3283 | 0.32829
135 | 75 | 1 | 75.8011 | 0.80112 | 135 | 51 | 1 | 51.3619 | 0.36192
140 | 77 | 2 | 76.9356 | -0.064419 | 140 | 52 | 1 | 52.3773 | 0.37729
145 | 78 | 1 | 78.0475 | 0.047494 | 145 | 53 | 1 | 53.377 | 0.37703
150 | 79 | 1 | 79.1392 | 0.1392 | 150 | 54 | 1 | 54.3636 | 0.36355
155 | 80 | 1 | 80.2129 | 0.21287 | 155 | 55 | 1 | 55.3391 | 0.33913
160 | 81 | 1 | 81.2705 | 0.27054 | 160 | 56 | 1 | 56.3058 | 0.30584
165 | 82 | 1 | 82.3141 | 0.31405 | 165 | 57 | 1 | 57.2656 | 0.26561
170 | 83 | 1 | 83.3451 | 0.34514 | 170 | 58 | 1 | 58.2202 | 0.22018
175 | 85 | 2 | 84.3654 | -0.63462 | 175 | 59 | 1 | 59.1712 | 0.17118
180 | 86 | 1 | 85.3762 | -0.62378 | 180 | 60 | 1 | 60.1201 | 0.12007
185 | 87 | 1 | 86.379 | -0.62102 | 185 | 61 | 1 | 61.0682 | 0.068168
190 | 88 | 1 | 87.3749 | -0.62514 | 190 | 62 | 1 | 62.0167 | 0.016669
195 | 89 | 1 | 88.3649 | -0.63506 | 195 | 63 | 1 | 62.9666 | -0.033363
200 | 90 | 1 | 89.3502 | -0.64982 | 200 | 64 | 1 | 63.919 | -0.080984
205 | 91 | 1 | 90.3314 | -0.66856 | 205 | 65 | 1 | 64.8746 | -0.12537
210 | 92 | 1 | 91.3095 | -0.6905 | 210 | 66 | 1 | 65.8342 | -0.1658
215 | 93 | 1 | 92.285 | -0.71499 | 215 | 67 | 1 | 66.7983 | -0.20165
220 | 93 | 0 | 93.2586 | 0.25857 | 220 | 68 | 1 | 67.7676 | -0.23243
225 | 94 | 1 | 94.2306 | 0.23064 | 225 | 69 | 1 | 68.7423 | -0.2577
230 | 95 | 1 | 95.2017 | 0.20166 | 230 | 70 | 1 | 69.7229 | -0.27714
235 | 96 | 1 | 96.172 | 0.17196 | 235 | 71 | 1 | 70.7095 | -0.2905
240 | 97 | 1 | 97.1418 | 0.1418 | 240 | 72 | 1 | 71.7024 | -0.2976
245 | 98 | 1 | 98.1114 | 0.11138 | 245 | 73 | 1 | 72.7017 | -0.29835
250 | 99 | 1 | 99.0808 | 0.080833 | 250 | 74 | 1 | 73.7073 | -0.29272
300 | 108 | 9 | 108.763 | 0.76303 | 300 | 84 | 10 | 84.0804 | 0.080363 | CHART A-2
350 | 118 | 10 | 118.2767 | 0.27673 | 350 | 95 | 11 | 94.7767 | -0.22331
400 | 128 | 10 | 127.3107 | -0.68932 | 400 | 105 | 10 | 105.3158 | 0.31582
450 | 135 | 7 | 135.6136 | 0.61361 | 450 | 115 | 10 | 115.2842 | 0.28415
500 | 143 | 8 | 143.1362 | 0.1362 | 500 | 124 | 9 | 124.5116 | 0.51155
550 | 150 | 7 | 150.0636 | 0.063604 | 550 | 133 | 9 | 133.139 | 0.13896
600 | 157 | 7 | 156.7386 | -0.26137 | 600 | 142 | 9 | 141.5769 | -0.4231
650 | 164 | 7 | 163.4756 | -0.52441 | 650 | 151 | 9 | 150.3551 | -0.64494
700 | 170 | 6 | 170.2648 | 0.26476 | 700 | 160 | 9 | 159.8627 | -0.13731
750 | 176 | 6 | 176.3675 | 0.3675 | 750 | 169 | 9 | 169.98 | 0.98002
800 | 180 | 4 | 179.802 | -0.19804 | 800 | 180 | 11 | 179.6007 | -0.39933
850 | 185 | 5 | 186.902 | 1.902 | 850 | 185 | 5 | 186.902 | 1.902 |  | % Flushometer: | 0
900 | 193 | 8 | 193.38 | 0.38004 | 900 | 193 | 8 | 193.38 | 0.38004
950 | 200 | 7 | 199.8163 | -0.18369 | 950 | 200 | 7 | 199.8163 | -0.18369
1000 | 207 | 7 | 206.2108 | -0.7892 | 1000 | 207 | 7 | 206.2108 | -0.7892
1050 | 212 | 5 | 212.5635 | 0.56351 | 1050 | 212 | 5 | 212.5635 | 0.56351
1100 | 219 | 7 | 218.8744 | -0.12555 | 1100 | 219 | 7 | 218.8744 | -0.12555
1150 | 224 | 5 | 225.1436 | 1.1436 | 1150 | 224 | 5 | 225.1436 | 1.1436
1200 | 231 | 7 | 231.371 | 0.37098 | 1200 | 231 | 7 | 231.371 | 0.37098
1250 | 238 | 7 | 237.5566 | -0.44341 | 1250 | 238 | 7 | 237.5566 | -0.44341
1300 | 244 | 6 | 243.7004 | -0.29959 | 1300 | 244 | 6 | 243.7004 | -0.29959
1350 | 250 | 6 | 249.8025 | -0.19754 | 1350 | 250 | 6 | 249.8025 | -0.19754
1400 | 258 | 8 | 255.8627 | -2.1373 | 1400 | 258 | 8 | 255.8627 | -2.1373
1450 | 262 | 4 | 261.8812 | -0.11878 | 1450 | 262 | 4 | 261.8812 | -0.11878
1500 | 269 | 7 | 267.8579 | -1.1421 | 1500 | 269 | 7 | 267.8579 | -1.1421
1550 | 275 | 6 | 273.7929 | -1.2071 | 1550 | 275 | 6 | 273.7929 | -1.2071
1600 | 281 | 6 | 279.686 | -1.314 | 1600 | 281 | 6 | 279.686 | -1.314
1650 | 287 | 6 | 285.5374 | -1.4626 | 1650 | 287 | 6 | 285.5374 | -1.4626
1700 | 293 | 6 | 291.347 | -1.653 | 1700 | 293 | 6 | 291.347 | -1.653
1750 | 298 | 5 | 297.1149 | -0.88515 | 1750 | 298 | 5 | 297.1149 | -0.88515
1800 | 302 | 4 | 302.8409 | 0.8409 | 1800 | 302 | 4 | 302.8409 | 0.8409
1850 | 308 | 6 | 308.5252 | 0.52518 | 1850 | 308 | 6 | 308.5252 | 0.52518
1900 | 313 | 5 | 314.1677 | 1.1677 | 1900 | 313 | 5 | 314.1677 | 1.1677
1950 | 319 | 6 | 319.7684 | 0.76839 | 1950 | 319 | 6 | 319.7684 | 0.76839
2000 | 324 | 5 | 325.3273 | 1.3273 | 2000 | 324 | 5 | 325.3273 | 1.3273
2050 | 330 | 6 | 330.8445 | 0.8445 | 2050 | 330 | 6 | 330.8445 | 0.8445
2100 | 336 | 6 | 336.3199 | 0.31988 | 2100 | 336 | 6 | 336.3199 | 0.31988
2150 | 341 | 5 | 341.7535 | 0.75349 | 2150 | 341 | 5 | 341.7535 | 0.75349
2200 | 347 | 6 | 347.1453 | 0.14532 | 2200 | 347 | 6 | 347.1453 | 0.14532
2250 | 352 | 5 | 352.4954 | 0.49538 | 2250 | 352 | 5 | 352.4954 | 0.49538
2300 | 358 | 6 | 357.8037 | -0.19635 | 2300 | 358 | 6 | 357.8037 | -0.19635
2350 | 363 | 5 | 363.0702 | 0.070154 | 2350 | 363 | 5 | 363.0702 | 0.070154
2400 | 369 | 6 | 368.2949 | -0.70512 | 2400 | 369 | 6 | 368.2949 | -0.70512
2450 | 373 | 4 | 373.4778 | 0.47782 | 2450 | 373 | 4 | 373.4778 | 0.47782
2500 | 378 | 5 | 378.619 | 0.61899 | 2500 | 378 | 5 | 378.619 | 0.61899
2550 | 383 | 5 | 383.7184 | 0.71838 | 2550 | 383 | 5 | 383.7184 | 0.71838
2600 | 388 | 5 | 388.776 | 0.77599 | 2600 | 388 | 5 | 388.776 | 0.77599
2650 | 393 | 5 | 393.7918 | 0.79182 | 2650 | 393 | 5 | 393.7918 | 0.79182
2700 | 398 | 5 | 398.7659 | 0.76588 | 2700 | 398 | 5 | 398.7659 | 0.76588
2750 | 403 | 5 | 403.6982 | 0.69816 | 2750 | 403 | 5 | 403.6982 | 0.69816
2800 | 409 | 6 | 408.5887 | -0.41134 | 2800 | 409 | 6 | 408.5887 | -0.41134
2850 | 414 | 5 | 413.4374 | -0.56261 | 2850 | 414 | 5 | 413.4374 | -0.56261
2900 | 419 | 5 | 418.2443 | -0.75566 | 2900 | 419 | 5 | 418.2443 | -0.75566
2950 | 424 | 5 | 423.0095 | -0.99049 | 2950 | 424 | 5 | 423.0095 | -0.99049
3000 | 429 | 5 | 427.7329 | -1.2671 | 3000 | 429 | 5 | 427.7329 | -1.2671
Note on B2: For reference
Note on C2: For reference
Note on E2: For reference
Note on G2: For reference
Note on H2: For reference
Note on J2: For reference